Change Order Request

February 5, 2015

Chinn Construction, LLC

14715 NE 95th Street, Suite 101

Redmond, WA 98052

Attn: 	Charlie Poggemann

Re:	Legacy Apartment Project – Change Order Request #01R

Charlie,

Per EN drawings dated 10/13/14 and C301 dated 8/17/14, changes were made to the sub-slab drainage and ventilation piping.  A list of changes and pricing is below.  Also, per request from Chinn Construction, we have included pricing for a simplex pump system, duplex pump system, and venting from room P-025 to the roof.

- Change the 4” schedule 40 PVC perforated mainline piping to 6” and increase piping quantities as shown on EN and C drawings: $7,262 + 10% OH&P = $7,988.

- Add 10ea airtight cleanouts to the foundation drainage and venting system: $1,274 + 10% OH&P = $1,401.

- Add 1ea Type 241 catch basin and 1ea 48” round pump basin to the foundation drainage system, including risers and lids as submitted: $3,840 + 10% OH&P = $4,223.

- Add 2ea 6” PVC vent tightlines from ‘trap detail’ to Room P-025 as shown on sheet EN2.0.  Lines will stub up in room at location specified by others.  $1,485 + 10% OH&P = $1,634.  Excludes test ports, monitoring ports and gate valves.

- Add 1ea 8” PVC vent from Room P-025 to the roof.  Includes 8ea PVC 90’s.  Routing to be determined by others.  $3,115 + 10% OH&P = $3,427.  Pricing assumes the line will be run in the most direct route from P-025 to roof.  Excludes all fans, equipment, monitoring ports, valves, vibration dampening attachments, etc.

- Add a 6” sewer connection in Room P-025 per Chinn Construction request.  Line will stub up in room at location specified by others.  $870 + 10% OH&P = $957.

- Add a pump line from the pump basin to Room P-025 per Chinn Construction request.  Line will stub up in room at location specified by others.  $551 + 10% OH&P = $606.  Excludes test ports, monitoring ports and gate valves.

- Add a Zoeller Model 161 SIMPLEX sump pump system to the foundation drainage system, including 3-float system with 50ft cords and control panel: $3,994 + 10% OH&P = $4,394.  Excludes all electrical work, installation of control panel, flow restrictors, explosion proof pumps, etc.

- Add a Zoeller Model 161 DUPLEX sump pump system to the foundation drainage system, including 3-float system with 50ft cords and control panel: $5,827 + 10% OH&P = $6,409.  Excludes all electrical work, installation of control panel, flow restrictors, explosion proof pumps, etc.

All pricing above excludes hoisting and excavation/backfill. The following details on sheet EN2.0 are specifically excluded: “Sub-slab depressurization system process and instrumentation diagram”, “Water treatment system process and instrumentation diagram”.  Please forward a Change Order at your earliest convenience.  Let me know if you have any questions or require further information.  Thank you.

Sincerely,

Richard Donelson

Project Manager / Estimator

LEED® Green Associate

richd@owpllc.net

425-591-4296 cell