## General Requirements:

  - Requirement of the “Built Green” Specification per Exhibit “D” as they relate to this scope of work.  (Mike, this is pending, we do not have this information yet.) Charlie, this could add costs depending on requirements to meet Built Green.

  - This Contract includes but is not limited to; all design, engineering, coordination, plan review, permits, labor, materials, supplies, tools, licenses, insurance, subcontracts, equipment, hoisting and other incidental items necessary to complete all Design Build Plumbing:

    - Supply a full time superintendent experienced in this type of site earthwork mixed use plumbing systems.

    - Contract amount includes all costs for mobilization for Subcontractor’s work in and out of the project.

  - Subcontractor acknowledges that the project is located in Mercer Island and no parking provisions will be supplied by the Contractor during the construction duration. (Mike, we are securing no-cost parking at the State Farm Insurance property a couple blocks away)

    - Storage space at the project site is very limited so off-site storage of materials will be necessary. Materials and equipment delivered to the project must be place in their designated scheduled position. Upon completion of the Parking Levels, some space will be available for a limited amount of material storage and the additional needed handling is part of the scope and cost of the subcontract.

- Furnish and install all PLUMBING work including but not limited to:

  - This will include but may not be limited to a complete design build water supply system comprising of a domestic cold water system and central domestic gas fired hot water heaters (includes (3) AO Smith BTH500, 130-gallon) boiler controls and storage tanks for the re-circulating hot water supply system, a complete working waste system and drainage system and gas piping delivery system within the building.

  - Provide for all required ADA dimensioning and clearances as it relates to plumbing.

  - Provide a complete drainage system inside the building. This will include but may not be limited to all roof, patios, decks, courtyards, garage, sub-slab drains, footing drains and trench drains. Included in this system will be the necessary pumps and piping interfaced with the utility structures in the parking garage.  Drains beyond the building footprint by others.

  - Provide plumbing design drawings as a submittal for coordination of your work and coordination with work by others.  Provide detailed dimensioned layout drawings on Cad to identify all service locations and sizes of sleeves that occur in each of the post tensioned concrete slabs.

  - All excavation and backfill for below grade rough plumbing and sub-rough drainage system by others.   Hoisting of concrete basins at slab on grade to be supplied by others.

  - Provide a complete waste system and determine the point of connection to the City sanitary sewer system exit from the building and make connection, if the stub is installed.

  - Identify all waste and venting risers needed so as to enable the necessary coordination and for proper framing and enclosing of the waste system within the wall systems. Show call outs for 2x6 or 2x8 walls needed for proper enclosing of the drainage system.

  - Provide and secure City of Mercer Island plumbing permit for the project, inspections, temporary water hookups and distribution of temporary water throughout the building for the purposes of testing the plumbing installations. Make the necessary temporary piping installation to discharge all test waters out of the building.

  - Supply and install all Link-Seals as required for your plumbing scope of work.

  - Supply and install all fire rated sleeves (ProSet) at all fire rated concrete assemblies.

- Domestic Water System

  - Provide and install a complete working hot and cold domestic water system. Hot water supply and return lines shall be insulated.

  - Provide and install central water heater system including, but not limited to, gas fired water heaters, expansion tanks, mixing valves, circulation pumps with pump controls, pipe insulation for the looped hot water system, gas supply and venting.

  - Furnish and install duplex, variable speed domestic water pressure booster package.

  - Water piping to be CPVC for 2.5” and larger pipe.  2” and small will be PEX.

  - Provide and install all backflow devices required for residential, common and retail locations.

  - Provide and install mop sinks with wall hung faucets in all (3) janitor rooms.

  - Make the final connection to the water meter stub.

  - Provide and install all piping, strapping, nail plates and any and all devices necessary to provide a complete working water system.

  - Provide all block outs and sleeving through concrete floors using Proset fire rated cans, the foundation walls or through concrete shear walls and cuts outs and coring of wood framing members necessary to complete the installation requirements.

  - Provide and install ten (10) keyless hose bibs in the garage and mechanical rooms.  Final location to be coordinated with Owner.

  - Provide and install ten (10) frostproof keyless hose bibs with recessed box at exterior locations.

  - Provide and install keyless hose bib with hot and cold water supply at the level P trash room.

  - Provide and install a main building shut-off valve and individual unit shut off valves.

  - Provide all expansion joints in the boiler line domestic hot water system as required by the manufacturer.

  - Provide and install a DCVA as required by the City of Mercer Island. Provide the certified test of the DCVA. Provide PRV if required.

  - Provide and install pipe insulation on all water piping outside the insulated or heated spaces or as required by Uniform Building and Plumbing code.

  - Supply and install water line and backflow device to be connected to trash chute.

  - Provide rough-in for future installation of unit meters on the hot and cold water supply lines within each individual unit.  The supply and installation of unit water meters are by others.

- Waste and Venting System

  - Provide and install a complete working waste system.

  - All horizontal and vertical waste lines will be constructed with ABS or PVC.

  - All roof drain lines to be ABS or PVC within the units.

  - Provide and install all piping, strapping, nail plates, supports and any and all devices necessary to provide a complete working waste and vent system.

  - Provide and install all block outs and sleeving through concrete floors using Proset fire rated cans, the foundation walls or through concrete shear walls necessary to complete the installation requirements.

  - Provide and install all condensate drain piping complete (excludes condensate pumps if required at HVAC units).

- Courtyard Drainage, Patio Drainage, Garage Drainage, and Roof Drainage System

  - Provide and install complete working roof rain water drainage, patio drainage, courtyard drainage, footing drains and sub slab drain within the building footprint.

  - This includes all drainage structures including, control structure, manholes, sand/oil catch basin and  foundation/sub-slab settling catch basin will be supplied and installed by subcontractor. All piping and materials complete with interconnection complete with controls are furnished and installed by this subcontract.

  - Provide and install sub slab and foundation drains within the building foot print.  Gravel backfill and fabric by others.

  - Connect to drain weeps at perimeter walls and connect to building drainage system.  All pipe penetrations, drain fabric and grates by others.

  - Provide and install all garage floor drains and trench drains located at the garage. Trench drains included are located at the garage entry and loading dock bay.  These drains will be set to finished concrete grade (allowing for slopes in concrete) and be provided with frames and grates capable of handling vehicular traffic.

  - Provide and install concrete sand/oil basin and concrete garage floor drains. Set structures to finished concrete grade. Hoisting of concrete basins to be supplied by others.

  - Provide and install all required drainage in each parking level, mechanical rooms and trash rooms.

  - Provide and install all required deck drains for exterior plazas, amenity spaces, etc. located within the building footprint at the level 2 and level 3 post tensioned decks.

  - Provide and install all drain and trench drain piping located within the building footprint to discharge into the required oil/water separator catch basin required for the operation of this drainage system.

  - Excavation, backfill, fine grading and compaction will be by this subcontractor for all plumbing work. All block outs or sleeving needs through the foundation walls or through the slabs necessary to complete this installation is by this plumbing scope of work using Proset fire rated cans.

  - Provide and install all drains per architectural drawings. Coordinate the drains and supply lines with the planter forming, waterproofing and concrete paver installations.  No drains included inside planters.

  - Provide and install floor drains where required. Special attention to the trash room and Sprinkler Room.

  - Provide for temporary drains and or connections to control rainwater to the completion of the roof drain systems.

  - All roof drainage overflow lines are to be plumbed within the framed walls and connect to drainage lines in the vertical wall.  All roof drains are to have an integral overflow contained in the same roof drain assembly.

- Retail / Tenant Improvement Space

  - Provide and install six (6) 4” waste, 3” vent and 1.5’ cold water to tenant spaces.

- Plumbing Fixtures

  - Provide and install all final plumbing fixtures to include all toilets and seats, lavatories, sinks, kitchen sinks, bath tubs, shower stalls, shower bases, seismic strapping/hold downs, hot water tanks, expansion tanks, handicap fixture requirements, drain assemblies, required floor drains, dishwasher connection, garbage disposal install (disposal to be furnished by others), clothes washer rough-in boxes, dishwasher air gaps, handicap pipe covers where required, water pipe insulation where required, trap primers, all double check valves required for proper operation of plumbing fixtures, ice maker boxes, final trim of any drains including the roof and garage drain grates.  Fixtures included as noted below:

Residential units:

white Toto CST416M dual flush toilet w/Toto SS114 seat

white Toto CST744EL, 17” high ADA elongated toilet w/Toto SS114 seat

white Toto LT502 china lavatory sink w/ Grohe 34.270.001 chrome faucet

white Superior 101C tub/shower stall w/Moen 62365 /TL183EP chrome valve

white Superior 100H tub/shower stall w/grab bars and seat w/Moen 62365 /TL183EP chrome

chrome Moen 52710 hand held shower at type A unit bathtubs

white Superior 48C-N shower stall (not adaptable) w/ Moen 62365 /TL182EP chrome valve

white Superior 48BF-FWA shower stall (adaptable) w/ Moen 62365 /TL182EP chrome valve

Moen G20192, 21”x16”x7.5” undercounter stainless steel sink w/Moen 7594 chrome faucet

Moen G18195, 21”x16”x5.5” ADA undercounter stainless steel sink w/Moen 7594 chrome faucet

Common areas:

white Toto CST744EL, 17” high ADA elongated toilet w/Toto SS114 seat

white Toto LT502 china lavatory sink w/Toto TL416SD-CP chrome faucet

Moen G18195, 21”x16”x5.5” ADA undercounter stainless steel sink w/Moen 7594 chrome faucet

  - Final dishwasher plumbing connections are included.  Electrical connections and final set and level of the dishwasher by others.

  - Fire rated, plastic clothes washer boxes are included.  Final connection to the clothes washer water plumbing connections by others.

  - Ice maker boxes are included.  Final connection to the ice makers by others.

  - Grohe 34.270.001 lavatory faucets are included.

  - All adaptable tub and shower surrounds shall have integral wood backing for future installation of grab bars (by others).

- Post Tension Deck Rough In and Piping penetrating “Rated Wall Assemblies”.

  - Provide all necessary material and labor to install any and all rough in sleeving necessary for all portions of the plumbing system. Others will provide the floor / wall layout but all sleeves or penetrations will be laid out, supplied and positioned by this plumbing contract. The sleeving and penetrations must conform to requirements for fire ratings applicable to each slab. All sleeves are to match the slab height of the floor or wall thickness within which the sleeves occur. Coordinate with the concrete subcontractor and the framer and perform the installation so as to minimize schedule interruptions and the flow of the work.  Supply and install Proset fire rated cans in the PT decks.

- Irrigation Rough In

  - Provide all necessary rough in for a complete irrigation system.  Irrigation water supply is to be stubbed to the point of connection (POC) at level L3 deck.  Irrigation system water supply sized to allow the irrigation contractor adequate water supply for all planter locations.  Irrigation system at level 3 deck and exterior of building is to be by others.

  - Provide female threaded terminations for irrigation contractor’s use during hook-up. A cap is to be placed on each stub to allow proper pressure testing.

- Gas Piping

  - Provide and install a complete network of gas piping within the building to service the following items of equipment, all central domestic water heaters, (4) roof top HVAC, (1) roof top BBQ and (1) fireplace.  All gas supply includes connection to the unit served with shut off valves.

  - All gas piping to be extended from the meter location and piped through the building to the needed riser locations. All gas piping within the building is to be labeled for ease of identification and in code compliance by this subcontract.

- Misc. Inclusions/Clarifications

  - Provide engineered, stamped drawings.

  - Provide labeling of all systems located in parking garage and at all risers and at all access panel locations.

  - Provide cleanout covers on all cleanouts located in finished walls and ceilings.

  - Provide tub liners for all bathtubs.

  - Provide access panels for your work, if required.  Unit access panels are excluded.

  - Provide necessary scaffolding, lifts, ladders (other than the tower crane supplied and operated by CHINN) and means and methods to access and install the plumbing scope of work.

  - No anchors are to be powder driven into Post Tension concrete floor slabs. All anchors are to be inserted prior to concrete pours or ONLY approved drill-in inserts are to be used with a MAXIMUM penetration of ¾”.

  - Carry out all flushing of domestic water systems.

  - Supply and install all counter flashings for all vent roof penetrations and supply. Set all roof drains in coordination with roof insulation and membrane installation.

  - Coordination of installation with other trades including the sink cutout templates for countertops. Provide all needed templates to the Millwork and tile subcontractors.

  - Sleeves are to be of Proset fire rated sleeves. Additionally, this subcontract to provide “a pour watch” to make corrections on any movement and proper alignment of sleeves during concrete placement operations.

  - Provide hot and cold water unit deduct meter installation (supply by others).  Install hot and cold water unit shut off valve to each unit and coordinate with the subcontractor providing and installing the individual unit water metering system (Ista or approved equal).  Install meter bases or meter unions supplied by Ista or others during roughin.

  - Supply and install all condensate lines for HVAC units.  (excludes condensate pumps if required at HVAC units).

  - Supply and install trench drains inside building.

  - Supply and install all backwater valves, RPBD’s, PRV’s, hose bibs, floor drains, oil / water separators, tub protectors, catch basins, grates, drain covers, area drains, roof drains.

  - Provide ProSet fire rated sleeves at PT decks where applicable (some penetrations; tubtraps, small water lines, and 1 ½” vents will need to be fire stopped by others).

  - Subcontractor shall maintain record drawings on a daily basis.

  - Maintain access to adjacent homes and business at all times.

  - Provide as-builts of all utility work.

  - Attend the City of Mercer Island pre-construction meeting.

  - All adjacent surfaces that are disturbed by Subcontractor’s work shall be restored to pre-existing conditions.

  - CHINN will supply all staking one time only.  Subcontractor is responsible for replacement of any staking lost due to their negligence.

  - Subcontractor acknowledges that there will be no delay costs for downtime due to inclement weather, discovery of unsuitable materials, discovery of unforeseen buried conditions, delays caused by the jurisdictions having authority, delays caused by the soils engineer or any other conditions beyond the control of CHINN.

  - Subcontractor shall respect the work and materials of other trades at all times, and shall take all necessary precautions to avoid damaging such work or materials.  If such work or material is damaged by Subcontractor, repairs shall be made at the expense of Subcontractor.

  - Subcontractor shall remove all trash, scraps, construction debris, and excess material of their craft from the work area on a daily basis.

  - Any material disturbed by the work described herein shall be protected from the effects of adverse weather by Subcontractor.

  - Subcontractor to clean all tires of silt and mud before entering roadways & right of ways.

  - All mobilizations in or out of equipment shall be coordinated with the site superintendent.

- Project Schedule and Activity Duration:

  - Shop Drawings and Submittals:

    - Provide shop drawings one six weeks following receipt of Subcontract.

    - Provide all submittals by one six weeks week following receipt of Subcontract.

    - Resubmit all items within five working days after being returned for correction.

    - O&M manuals and each Owners unit manual to be available 8 weeks after submittal approvals

  - Sequencing and Schedule Milestones:  The schedule will be mutually agreed upon, with the understanding that five days after the roof is framed, the plumbing vents and drains for the entire building will be complete.  The 3 week schedules will be updated frequently throughout the project.

- Exclusions:

  - Excavation, backfill, fine grading and compaction for all plumbing work.

  - Prevailing wages

  - Fire stopping.

  - PT wall layout.

  - Heat trace tape.

  - Water meters.

  - Pipe guards.

  - Gas meters.

  - Waste disposal fees.

  - Alarm or electrical wiring.

  - Wrapping of waste, vent or drain stacks, elbows and wyes with sound padding.

  - Installation of cans on PT deck after cables and rebar.  Plumbing subcontractor must install prior to rebar and PT cables.

  - Insulation / Heat tracing other than what is included above.

  - Water meters.

  - Gas meters.

  - Fire sprinklers.

  - Sheetrock removal and patching.

  - Pump systems other than boilers.

  - Backflow devices for irrigation and fire sprinkler systems.

  - Irrigation piping other than what is listed above.

  - HVAC piping other than what is listed above.

  - HVAC.

  - Tenant improvement retail area gas piping.

  - Grease interceptors or grease waste piping.

  - Housekeeping base for hot water heaters

  - Wash machine drain pans.

  - Tower crane fees.

  - Grab bars and seats other than the ADA tubs.

  - PT slab layout of walls.

  - Cutting and drilling holes in countertops.

  - Backing for wall hung fixtures.

  - Electrical wiring.

  - Pipe guards and shields in the garage.

  - Disinfection of water lines within the building other than flushing.

  - WSST.

  - Retention above 5%.

  - Performance or payment bonding

- Change Orders

  - Change orders are to be approved in writing prior to starting/commencing work. All Change Orders that are    initiated by a change in the contract drawings must be approved in writing and issued to Contractor within 5 days of receipt of the new contract documents. Change Orders not recognized within this 5 day period will not be the responsibility of the contractor.

- Option Pricing

  - The following options may be added or deleted form the scope of work by Change Order.

    - Add pipe insulation from corridor to “point of use” within units	$48,200.00

    - Upgrade to Galvanized Metal Washer Boxes (non fire-rated)	$22,900.00

    - Install 1.28 single flush toilets in lieu of dual flush	($19,300.00)

    - Furnish Only Unit Access Panels	$19,920.00

- Contract Amount

CODE	DESCRIPTION	VALUE

2200-220000	Plumbing (less fixtures and subslab drainage)	$2,261,900.00

2200-220000	PVC waste stacks in lieu of cast iron - credit

Residential Units	($121,400.00)

Retail and Amenity Spaces	($17,200.00)

2200-220000	Ice Maker Boxes	$32,700.00

2200-220002	Footing Underslab Drainage	$48,600.00

2200-220003	Plumbing Fixture Allowance	$280,800.00

2200-220003	Grohe 34.270.001 Lav Faucets	($15,900.00)

TOTAL CONTRACT AMOUNT	$2,469,500.00

End of Exhibit A