MEP COORDINATION MEETING MINUTES

# PROJECT:	 Hadley Project / Legacy Mercer Island – Mixed Use

# LOCATION:	 Legacy Conference Room – Mercer Island

# MEETING DATE:	 07/23/15

# ATTENDEES: 	Steffenie Evans – Legacy			Roger Sawicki – Legacy

# Sarah Argudo – Legacy				Richard Crawford - IEC

# Sim Mooers – CHINN				Richard Donelson - OWP

# Lauren Bjorndahl – CHINN			Brett Mortimore - OWP

# John Studioso – IEC				Gary Breiwick – Advanced Fire

# Andrew Earle – Froula				Shaun Clancy - CFM

# Charlie Poggemann – CHINN			Mark Pesanti - CHINN

HVAC:

- Garage Ventilation

  - Below Grade exhaust tunnel

    - Acoustic Consultant

  - Plumbing has approx. 8 – 8” pipes running through tunnel, but not in concrete opening

  - CFM changing manuf. Garage EFs

    - HP will increase to 7.5 and (1) at 5HP

- Fitness Room – 324

  - Designed with an in wall ac unit changing to a ductless unit and fan for fresh air

- Stairs 1 and 3 are pressurized – LB to submit product data on fans.

- Updated HVAC plans were uploaded to dropbox

  - Review sheet M2.1 for corrections

Plumbing:

- Corridor (shear) Walls and plumbing Walls

  - Being addressed with panel shops

- Boiler intake/vent routing

- Plumbing fixture

  - Need common area lav

    - Legacy requested modern look that is ADA compliant

  - Need decision on kitchen faucet

    - Legacy requested to hold 10k of Grohe faucet. OWP to try and hold price for two months

- Repeaters for unit Hot water metering only, spacers to be installed on cold.

  - Legacy/Yardi to locate repeaters

- Irrigation at roof/hose bib

  - Irrigation - Price out running pipe to roof from deduct meter *preferable method

  - Irrigation – If pulled off domestic line a backflow preventer must to be installed

  - Hose bib – Above toilet room in Amenity space, CHINN to review hose bib location at roof with VIA.

Fire Sprinkler:

- 3rd Floor – 4” and 6” pipes runs going through corridor.

  - Needs 7” clear down corridor

- No Heat Trace Allowed

  - RFI 118 proposed new routing – This routing will be proposed to COMI Fire Marshal on 7/27

- A standpipe in 327 closet to get into stairwell – ok Legacy

- FM comments – Add hose valves at the courtyard

  - Advanced to address locations after meeting with FM on 7/27

Low Voltage:

- Permit Status

- IDF – in Room P025

- Updated drawings – send to Legacy

  - SE marked up unit plans for jack locations

  - Froula needs locations for common area, Leasing, Fitness and Media

- Low Voltage Head End for Access System – Room 215

- Meeting with Franchise utilities

  - Schedule with Legacy Partners – in progress

  - Comcast Smart panels 14”x30” – review panel shop drawings

  - Legacy requested pricing (1) fiber, (1) RG6, (2) Cat5

Electrical:

- Added storage rooms in Parking level

- Product submittals

- Permit Status

- Outlets at decks

- Fixture E12 at roof top – LB send to SE

- Corridor Can Lights/L 25 Disk Light – L25 Disk Light is acceptable

Other:

- Review 2nd floor ceiling finish, height, and soffit height

  - Lowest point is plumbing

- Added storage rooms

  - Wall construction between units

  - Must be chain-link at top

- Door Swings

  - Coordinate with MEP

- MEP Equipment Rooms

  - Electrical and Low Voltage only

- What rooms at Level P through Level 2 need to be framed first?

  - IEC would like to get equipment in room before wall framing is completed

- ASIs

  - ASI 2 – Plumbing Walls

  - ASI 3 – Elevator Machine room Swap

  - ASI 4 – Unit A Plan Closets

  - ASI 5 – ADA Storage Room

  - ASI 6 – Change wall lengths

  - ASI 7 – Package Lockers

  - ASI 8 – Heated Sprinkler Space, Doors, Room P021

    - Add wall between water treatment and electrical equipment

    - Keep pairs of doors for P021 and P025A, do not include panic hardware at these locations

- Elevator Machine Room 1 and 2 – plumbing and low voltage lines

Meeting Adjourned: The preceding minutes are CHINN Construction’s interpretation of the items discussed and decisions reached at the above referenced meeting. Any persons desiring to add to, or otherwise change the minutes, are asked to correct the written statement or submit their comments in writing to CHINN Construction within two (2) days; otherwise the Minutes will stand as written.