May 19, 2016

Exxel Pacific

4220 Aurora Avenue N.

Seattle, WA 98103

Attn: 	Jola Bielecki

Re:	The Cora – OWP Submittal Narrative

Jola,

The materials being submitted in our plumbing material submittal and the stamped, engineered drawings conform to local building and plumbing codes, building standards, and engineering standards.  We’ve used the same or similar products, and drawn our projects the same way on 20+ similar mixed-use multi-family projects that we’ve completed in the past 5 years, with no issues arising.

We have used Franklin Engineering’s services exclusively for plumbing engineering for our design-build projects for over 10 years.

One Way Plumbing has seen many different plumbing materials come and go for the last 35+ years, and we have used our experience and history to select the most dependable and efficient materials that exist today.  When selecting our materials and how we design a project, we try to consider the lifespan of the building, ease of maintenance, functionality for the building and its tenants, etc.  Here are some examples:

Materials:

- Pex is used for water piping over CPVC or copper because it has nearly eliminated all leaks caused by workmanship, the fittings cannot be dry fit, it’s acoustically superior because it reduces water hammer and rushing water noise, it is resistant to freeze damage, and it’s more cost effective and stable in price.  Pex is available in up to 3” size, so everything 4” or larger within the garage will be CPVC, which has been used successfully within the industry for many years.

- Copper piping and copper ‘press’ type fittings are used in the boiler room because it provides a rigid, cleaner, consistent layout and appearance.  Press type fittings are used over soldered fittings because it has nearly eliminated all leaks caused by workmanship and provides a more dependable connection.

- Cast iron piping is being used at all waste and roof drain stacks wherever acoustical properties are important, such as units, retail, amenity and common spaces.  Cast iron has superior acoustical properties to PVC or ABS piping.

- PVC piping is being used at all vent and garage piping, and all rain leader overflows, because acoustical properties are not important.  PVC is being used over ABS pipe because it provides a cleaner look (ABS can sag in between hangers).

- Sleeved pex piping will be used within PT slabs and pop-up into walls, which reduces the amount of piping within walls that could potentially be damaged, reduces drilling of the framed structure, and reduces the number of fittings used within the system.

Engineered, stamped drawings:

- Two backflow preventers are shown on the main domestic water supply.  This is not required by any plumbing code, nor is it industry standard.  One Way Plumbing does this so that the building does not need to be shut down when the backflows are certified each year.

- Two circ pumps are shown on the main building hot water circulation supply.  This is not required by any plumbing code, nor is it industry standard.  One Way Plumbing does this so that if one pump fails or needs service, the other pump will provide hot water to the building while the other pump is serviced.  We provide a Tekmar control box that alternates the two pumps every ~20 hours to prevent uneven wear.

- Butterfly valves will be used within the boiler room and water main, which are much easier to turn than other valves, making it easier for maintenance to shut off the water when needed.

- MEP meetings have been conducted to coordinate each system with each other and the structural and architectural requirements of the building.

Please let me know if you have any questions or require further information.  Thank you.

NOTE: The information contained in this memo is considered trade knowledge/secrets.  It is expected that this document remain confidential to only the GC, Architect and Owner, and only be used for the Cora Project.

Sincerely,

Richard Donelson

Project Manager / Estimator

richd@owpllc.net

425-591-4296 cell