## UNDERGROUND & GARAGE MATERIALS
PROJECT: THE CORA APARTMENTS
UNDERGROUND & GARAGE SUBMITTALS - ONE WAY PLUMBING LLC
TAG | DESCRIPTION:
FD-1 | GARAGE FLOOR DRAIN, Quality Concrete CB40, 20"x26"x30" concrete garage floor drain/basin. Install with heavy duty traffic rated iron frame and grate. Drain to oil/sand separator.
FD-2 | FLOOR DRAIN, ProSet P65X or Watts FD33, drain with heavy duty iron strainer assembly at water heater, fire sprinkler and 1st floor trash room.
FD-3 | FLOOR DRAIN, Watts FD15-R, cast iron drain with brass or ductile iron strainer assembly. Cast entire assembly into concrete deck.
DD-1 | DECK DRAIN, Watts FD15-R cast iron drain with clamping collar and adjustable ductile iron strainer assembly. Drain body to be cast into concrete deck. Clamping collar and strainer to be installed after waterproofing.
TD-1 | TRENCH DRAIN, NDS DS-090N, polyethylene trench with DS231 cast iron grate.
FCO | CLEAN OUT, Floor type, Watts CO20, cast iron adjustable cleanout with round ductile iron top and brass cleanout plug.
CS-1 | CONTROL STRUCTURE, detention storage flow control structure, Specified Fittings, LLC, with sanded PVC gasketed sleeve. NOTE: Please confirm waterproofing details. OWP can install a linkseal w/ grout in lieu of the sanded sleeve detail (reference detail 2/C0310).
OW-1 | OIL SAND SEPARATOR, 36"x36" concrete basin with H-20 rated frame and grate. Quality Concrete Products, Inc; Mukiteo, WA.
SP-1 | GARAGE DRAIN SUMP PUMP AND BASIN, Duplex. (serves garage and mech room floor drains) Submersible sump pump, including automatic level controls, high water alarm, & basin to fit application. Pump capacity: 78 GPM @ 20' TDH. Zoeller IX161, sump pump and Zoeller control panel. Catch Basin: Concrete, 60" diameter (Verify depth) with HD-20 wheel rated cover. Quality Concrete Products. Electrical Data: 200 volt/ 1 phase/ 8.8 amps/ 1/2-hp. EACH pump.
CB-1 | FOUNDATION DRAIN SILT BASIN, Concrete, 30"x34"x56" deep exterior size with HD-20 wheel rated cover. Quality Concrete Products type 241.
SP-2 | FOUNDATION DRAIN SUMP PUMP AND BASIN, Duplex. (serves foundation drainage) Submersible sump pump, including automatic level controls, high water alarm, & basin to fit application. Pump capacity: 66 GPM @ 20' TDH. Zoeller N140 series, 1 hp sump pumps and Zoeller alternator control panel. Catch Basin: Concrete, 60" diameter (Verify depth) with HD-20 wheel rated cover. Quality Concrete Products or approved equal. Electrical Data: 115 volt/1 phase/ 12.0 amps/ 1-hp . EACH pump.
BWV-1 | BACKWATER VALVE, Canplas, PVC DWV
MATERIAL DESCRIPTIONS:
SUMP PUMP PRESSURE PIPE: PVC Schedule 40 Pressure Pipe.
PERFORATED FOOTING/FOUNDATION DRAIN PIPING: Perforated PVC Schedule 40.
UNDERGROUND DRAIN, WASTE, VENT PIPING: PVC Schedule 40.
GARAGE DRAIN, WASTE, VENT PIPING: PVC Schedule 40.
PROSET SLEEVES: For penetrations through concrete decks.

## MATERIAL SUBMITTAL
PROJECT: THE CORA APARTMENTS
PLUMBING MATERIAL SUBMITTALS - ONE WAY PLUMBING LLC
MATERIAL | DESCRIPTION (IF NEEDED):
BALL VALVES
BUTTERFLY VALVES
CAST IRON PIPING | Cast Iron Piping and no-hub bands for use at waste and roof drain stacks in units, retail, amenity and common spaces.
COPPER PIPING | Only for use in boiler room.
CORZAN PIPING | Corzan CPVC Schedule 80 Piping. For use at domestic water main only, everything 4" and over (within garage only)
GAS PIPING | Schedule 40 Black Iron - Threaded
LINKSEALS | For use at utility penetrations into building.
PEX PIPING | For all water piping up to and including 3".
PEX PIPING - SLEEVED | For use within PT slabs. Includes pop-up supports.
PIPE HANGERS & SUPPORTS
PIPE INSULATION | Thermal insulation only on hot water circulation supply and return mains, only.
PVC PIPING | Schedule 40 PVC piping for use at all vent piping, roof drain overflows and garage piping.

## EQUIPMENT SUBMITTAL
PROJECT: CORA APARTMENTS
EQUIPMENT SUBMITTALS - ONE WAY PLUMBING LLC
TAG | DESCRIPTION:
BFP-1 | BACKFLOW PREVENTER, Reduced pressure type with shut-off valves. Watts Model 957OSY. Main domestic backflow preventer.
BFP-2 | BACKFLOW PREVENTER, Reduced pressure type with shut-off valves. Watts Model LF009. For use at domestic bypass and trash chute water supply.
BFP-3 | BACKFLOW PREVENTER, DCVA with shut-off valves. Watts Model 007. For use at irrigation.
BP-1 | BOOSTER PUMP & CONTROL PACKAGE, Tigerflow EX-3000-V-VFD-NSF duplex variable speed domestic water pressure booster package. 125-PSI maximum working pressure. Stainless steel suction and discharge headers with flanged system connections. Package to be mounted on a welded steel platform with an industrial grade paint finish. UL listed control panel, variable speed drives, system pressure transmitters and main power disconnect. Package inlet and outlet pressure gauges. Each pump shall have suction and discharge isolation valves and discharge check valve. Package is pre-wired for a single point power strike. Package capacity: 200GPM @ 21-PSI boost. Includes (2) variable speed pumps, 5.0HP, 3600 RPM, (1) 132-gallon ASME hydro pneumatic tank. Electrical data: 208/3/60, each pump motor (verify circuit size)
WH-1, 2 | WATER HEATERS, PVI model 40-L-130A-CGML, 130-gallon, up to 96% thermal efficiency, natural gas fired, 400 MBH input, PVC venting connections (combustion air & exhaust). Electrical data: 120, 60hz, 11.0 amps
WH-3 | WATER HEATERS, EEMAX MT007240T on-demand electric water heater for hot water supply at retail restroom lavatory only. Electrical data: 240 or 208 volt (see submittal)/1/60, 27.0 amps.
ET-1 | EXPANSION TANK - DOMESTIC WATER, tank volume = 15 gallons. Armstrong AST-30, potable water expansion tank.
CP-1, 2 | CIRCULATION PUMP, Domestic Hot Water system. Armstrong E series bronze circulating pumps for domestic hot water circulation. Tekmar 132 pump control. Pump capacity: 12 GPM @ 13' TDH. Armstrong E7.2B Electrical Data: 115/1/60, 1.5 amp circuit (each pump)
MV-1, 2 | MIXING VALVE, Thermostatic type. Two (2) Lawler Series 66-150 Lead free mixing valves, piped per manufacturer details and to meet final design of 46 GPM @ 5 PSI ∆P.
CBV | CIRCUIT BALANCING VALVE, Circuit Solver or Caleffi. Size per plans.
GPRV-1 | GAS PRESSURE REGULATOR, Maxitrol 325 series, see plan for sizes.

## BATH & SHOWER
PROJECT: CORA APARTMENTS
BATH AND SHOWER STALL SUBMITTALS - ONE WAY PLUMBING LLC
TAG | DESCRIPTION:
TS1 | BATHTUB/SHOWER COMBO, Aquatic 2603SMTE, 60"W x 33-1/4"D x 79-1/4"H exterior dimensions, 1-piece fiberglass tub/shower stall with backing for future grab bar installation.
TS2 | ADA BATHTUB/SHOWER COMBO, Aquatic 2603SMTE, 60"W x 33-1/4"D x 79-1/4"H exterior dimensions, 1-piece fiberglass tub/shower stall with grab bars and folding seat.
SS-1 | SHOWER STALL, type B units: Aquatic 1483EN, 48"W x 38-3/4"D x 77-3/4"H exterior dimension, 1-piece fiberglass shower stall with permanent curb threshold. Stall includes grab bar backing in fiberglass walls. Stall selection to be reviewed by architect to meet type B requirements.

## FIXTURES
PROJECT: CORA APARTMENTS
PLUMBING FIXTURE SUBMITTALS - ONE WAY PLUMBING LLC
QUESTIONS FOR GC/OWNER/ARCHITECT:
1. Please confirm that handshowers are not needed at live/work unit bathtubs.
2. Two options, with pricing, have been sent in for a bottle filler at the fitness room. Please confirm which one has been selected.
TAG | DESCRIPTION: | LOC:
WC-1 | WATER CLOSET, FLUSH TANK, Gerber 21-912EB, gravity flush tank, elongated front, 1.28 gpf, vitreous china, white. Seat: Bemis 1500EC, elongated front, with cover. LSP V104-A-LL brass angle stop and LSP SWC-112-PP braided stainless steel supply. | Type B Units
WC-2 | WATER CLOSET, FLUSH TANK, Gerber 21-918, gravity flush tank, ADA high, elongated, 1.28 gpf, vitreous china, white. Install to meet ADA as required. Seat: Bemis 1500EC, elongated, with cover. LSP V104-A-LL brass angle stop and LSP SWC-112-PP braided stainless steel supply. | Type A Units
WC-3 | WATER CLOSET, FLUSH TANK,Gerber 21-918, gravity flush tank, ADA high, elongated, 1.28 gpf, vitreous china, white. Install to meet ADA as required. Seat: Bemis 1955CT, elongated, open front less cover. LSP V104-A-LL brass angle stop and LSP SWC-112-PP braided stainless steel supply. | Amenity & Retail Restrooms
L-1 | LAVATORY, Lenova PU-01-W, undercounter, vitreous china, white. Faucet: Grohe 34.270.001, single lever, 1.5 gpm, with pop-up waste assembly. Dearborn P9704 p-trap and LSP V104-A-LL brass angle stops. | Type B Units
L-2 | LAVATORY, Lenova PU-01-W, undercounter, vitreous china, white. Faucet: Grohe 34.270.001, single lever, 1.5 gpm, with pop-up waste assembly. Dearborn P9704 p-trap and LSP V104-A-LL brass angle stops. Include insulation kit on p-trap and water supply to meet ADA.
L-3 | LAVATORY, Lenova PU-01-W, undercounter, vitreous china, white. Faucet: Grohe 34.271.001, single lever, 0.5 gpm, with grid drain waste assembly. Dearborn P9704 p-trap and LSP V104-A-LL brass angle stops. Include insulation kit on p-trap and water supply to meet ADA. | Fitness Restroom
L-4 | LAVATORY, Lenova PU-01-W, undercounter, vitreous china, white. Faucet: Grohe 34.271.001, single lever, 0.5 gpm, with grid drain waste assembly. EEMAX MT007240T on-demand electric water heater for hot water supply at retail restroom lavatory only. Dearborn P9704 p-trap and LSP V104-A-LL brass angle stops. Include insulation kit on p-trap and water supply to meet ADA. Electrical: 240v, 27 amp | Retail Restroom
TS-1 | BATHTUB/SHOWER COMBO, Aquatic 2603SMTE, 60"W x 33-1/4"D x 79-1/4"H exterior dimensions, 1-piece fiberglass tub/shower stall with backing for future grab bar installation. Tub/Shower Trim Kit: Delta T14459, chrome, single handle, 1.5 gpm shower head, diverter slip tub spout, with Delta R10000MF pressure balance valve. Tub drain kit: LSP R-6011RK/R0910 chrome waste and overflow assembly. | Type B Tubs
TS-2 | BATHTUB/SHOWER COMBO, Aquatic 2603SMTE, 60"W x 33-1/4"D x 79-1/4"H exterior dimensions, 1-piece fiberglass tub/shower stall with backing for future grab bar. Tub/Shower Trim Kit: Delta T14459, chrome, single handle, diverter slip tub spout, with Delta RPW324HDF-1.5 hand held shower and slide bar with Delta R10000MF pressure balance valve. Tub drain kit: LSP R-6011RK/R0910 chrome waste and overflow assembly. | Type A Tubs
SS-1 | SHOWER STALL, Aquatic 1483EN, 48"W x 38-3/4"D x 77-3/4"H exterior dimension, 1-piece fiberglass shower stall with permanent curb threshold. Stall includes grab bar backing in fiberglass walls. Tub/Shower Trim Kit: Delta T14259, chrome, single handle, 1.5 gpm shower head with Delta R10000MF pressure balance valve. Oatey 42097 PVC shower drain. | Type B Showers
S-1 | SINK, SINGLE BOWL KITCHEN SINK, Lenova LS18304 single bowl, undercounter, stainless steel. Faucet: Grohe 32.665.001, chrome, single lever handle with pull-down spray head, 1.75 gpm. Dearborn P9704 p-trap and LSP V104-A-LL brass angle stop. | Type B Units
S-2 | SINK, SINGLE BOWL KITCHEN SINK, type A units, Elkay ELUHAD2115-5 single bowl (5" deep), undercounter, stainless steel. Faucet: Grohe 32.665.001, chrome, single lever handle with pull-down spray head, 1.75 gpm. Dearborn P9704 p-trap and LSP V104-A-LL brass angle stop. Include insulation kit on p-trap and water supply to meet ADA. | Type A Units
S-3 | SINK, SINGLE BOWL, Kohler K-3894-4-NA single bowl, undercounter, stainless steel. Faucet: Grohe 32.665.001 at L1 kitchenette, chrome, single lever handle with pull-down spray head, 1.75 gpm. DELTA 9959-CS-DST FAUCET, BRONZE at amenity kitchen. Dearborn P9704 p-trap and LSP V104-A-LL brass angle stop. | Lobby & Amenity
DW | DISHWASHER, LSP V104-A-LL chrome angle stop with LSP KDW-660-PP flexible supply. Install Zurn CD4P plastic countertop mount airgap. | All Units
AW | WASHER CONNECTION - RESIDENTIAL TYPE, IPS WaterTite series recessed washer box kit with 2" drain, 1/2" hot & cold shutoff valves with hose connections and code approved water hammer arrestors. Install with rated box only where needed. | All Units
MOP | Mustee 63 fiberglass mop sink (24"x24"x10") with Mustee 63.600A wall mount chrome faucet. | Janitor 215
DBW | DOG/BIKE WASH, T&S Brass PG-8WREV wall hung hot and cold faucet with coiled polyurethane hose and aluminum spray head. Includes anti-syphon vacuum breaker. | P1
HB1 | HOSE BIBB, Woodford 65B, with recessed box, non-freeze, anti-siphon, vacuum breaker, automatic draining, loose key handle. Size: 3/4" | Street Exterior, see plans
HB2 | HOSE BIBB, Woodford 65, non-freeze, anti-siphon, vacuum breaker, automatic draining, loose key handle. Size: 3/4" | Deck Exterior, see plans
HB3 | HOSE BIBB, Woodford 24, anti-siphon - vacuum breaker, wheel handle and loose tee key. Mechanical rooms. Size: 3/4" | P1, see plans
HB4 | HOSE BIBB, Woodford 24, hot and cold hosebib at residential trash room with anti-siphon - vacuum breaker, wheel handle and loose tee key. Supply with tempered water thru Lawler tempering valve or equal. Size: 3/4" | Trash 211
HB5 | HOSE BIBB, Woodford RHY2-MS, roof hydrant with anti-siphon - vacuum breaker, lever handle. . Size: 3/4" | Roof, near dog run
RD-1 | ROOF DRAIN, Watts RD25, cast iron body, drain with overflow. Includes cast iron clamping collars and strainer. | Roof