Functional Test FT-8

Domestic Water Heater

Unit ID______________

| Project: | OLD TOWN MIXED USE |
| --- | --- |

| Date: |  |
| --- | --- |
| Tag: | WH |
| Building: |  |
| Location: | REDMOND, WA |

1.	Participants

| Party |  | Participation |
| --- | --- | --- |

Party filling out this form & witnessing _________________________  Date of test _________

2.	Test Prerequisites

a.	__ The following have been started up and startup reports and prefunctional checklists submitted and approved ready for functional testing:

__ PC-8 Domestic Water Heater

b.	__ All control system functions for this and all interlocking systems are programmed and operable per contract documents, including final setpoints and schedules and with debugging, loop tuning  and sensor and device calibrations completed.

_________________________________	_________________________

Controls Contractor Signature or Verbal		Date

c.	__ Piping system flushing complete and required report approved.

d.	__ n/a.

e.	__ n/a

f.	__ n/a

g.	__ All A/E punchlist items for this equipment corrected.

h.	__ These functional test procedures reviewed and approved by installing contractor.

i.	__ Safeties and operating ranges reviewed.

j.	__ Test requirements and sequences of operation attached.

k.	__ Schedules and setpoints attached.

l.	__ Sufficient clearance around equipment for servicing.

m.	__ Have all energy savings control strategies, setpoints and schedules been incorporated that this boiler and control system are capable of?  If not, list recommendations below.

Np.	__ Record made of All Values for Current Setpoints (SPt), Control Parameters, Limits, Delays, Lockouts, 
Schedules, Etc. Changed to Accomodate Testing:

3.	Functional Testing Record

a.	Perform functional testing of residential water heaters in 25% of the residential units (approx. 38 units). Provide separate Functional Test form for each unit. And indicate unit ID # on form.

a.

| Seq. ID From Specs1 | Mode ID2 | Test Procedure3 (including special conditions) | Expected Response4 | Pass Y/N | Note |
| --- | --- | --- | --- | --- | --- |
| 1 | Water Heater Setpoint | - Run kitchen faucet at 100% hot water for 60 seconds and measure water temperature | - 115°-120F Water temp - Record hot water temp ___________F |  |  |

Record Foot Notes

1Sequences of operation specified in Contract Documents (attached).

2Mode or function ID being tested, per testing requirements section of the project Specifications.

3Step-by-step procedures for manual testing, trend logging or data-logger monitoring.

4Include tolerances for a passing condition.

5Record any permanently changed parameter values and submit to Owner.

The functional performance tests are all successfully completed.                        ___ YES   ___ NO

-- END OF TEST --