## 1. PLUMBING FIXTURE
TAG |  | PLUMBING FIXTURE SCHEDULE
P1 |  | WATER CLOSET, FLUSH TANK, Kohler K3998, gravity flush tank, elongated bowl, 1.28 gpf, vitreous china, white. Seat: Bemis 1500EC or equal, elongated, with cover, white.
P2 |  | WATER CLOSET, FLUSH TANK at TYPE A UNITS, Kohler K3999, gravity flush tank, 17" high, elongated, 1.28 gpf, vitreous china, white. Install to meet ADA as required. Seat: Bemis 1500EC or equal, elongated, with cover, white.
P3 |  | LAVATORY, UNDERCOUNTER, Sterling 442040, 17x13, undercounter, vitreous china, white. Install to meet ADA as required. Faucet: Grohe 34 270 000, single lever chrome faucet with pop-up waste assembly. Faucet to be single hole mount.
P4 |  | NOT USED
P5 |  | BATHTUB, Sterling Accord 71140116, 60"Wx32"Dx18"H, Vikrell resin bathtub. Tub/Shower Trim Kit: Grohe 35 009 00E, chrome, single handle, 1.5 gpm shower head, tub spout, w/Grohe 35 015 000 pressure balancing mixing valve. Install Symmons H321-V chrome 1.5 gpm hand shower with slide bar at ADA units only.
P6 |  | SHOWER, Swan SS3448, 48"W x34"D x5.5"H, Swanstone resin shower pan. Shower Trim Kit: Grohe 35 010 00E, chrome, single handle, 1.5 gpm shower head, w/Grohe 35 015 000 pressure balancing mixing valve.
P7 |  | SINK, SINGLE BOWL, Dayton DXUH2115, 23"Wx17"Dx8"H, undercounter, 18-gauge stainless steel sink. Faucet: Grohe 32 665 00E, 1.5gpm chrome, single lever handle with pullout spray head. Faucet to be single hole mount.
P8 |  | SINK, SINGLE BOWL at TYPE A UNITS, Elkay ELUHAD2115, 23"Wx17"Dx5"H, undercounter, 18-gauge stainless steel sink. Faucet: Grohe 32 665 00E, 1.5gpm chrome, single lever handle with pullout spray head. Faucet to be single hole mount.
P9 |  | DISHWASHER CONNECTION - LSP V-104-A chrome angle stop with LSP KDW-660-PP flexible supply. Install Zurn CD4P plastic countertop mount airgap.
P10 |  | ICEMAKER CONNECTION - RESIDENTIAL TYPE, recessed box kit with 1/2"x3/8" cold shutoff valve and code approved water hammer arrestors.
P11 |  | WASHER CONNECTION - RESIDENTIAL TYPE, washer box kit with 2" drain, 1/2" hot & cold shutoff valves with hose connections and code approved water hammer arrestors.
P12 |  | ELECTRIC WATER HEATER- RESIDENTIAL TANK TYPE, AO Smith ECT-52, 50-gal. water heater with 4.5 kw non-simultaneous elements, 208 volt, 1 phase. Include Oatey aluminium drip pan under each heater. Include insulation pad to meet code. Include ProFlo PFXT5 expansion tank. Include earthquake strap kit.
P13 |  | LAVATORY, WALL HUNG, AMENITY, Kohler 2035-1, 22x18, wall hung lavatory sink with single hole, vitreous china, white. Faucet: Grohe 34 271 000, single lever chrome faucet with flow rate limiter and grid drain assembly.
P14 |  | SINK, SINGLE BOWL, AMENITY, Elkay ELUHAD2115, 23"Wx17"Dx5"H, undercounter, 18-gauge stainless steel sink. Faucet: Grohe 32 665 00E, 1.5gpm chrome, single lever handle with pullout spray head. Faucet to be single hole mount.
P15 |  | ELECTRIC WATER HEATER, (amenity faucets) Eemax SP4208, 4 KW, 208 volt, 1-phase electric wall hung on-demand heater to serve single amenity faucet each.
P16 |  | DOG WASH, Watts FD33 floor drain, cast iron body, with 8" ductile iron strainer assembly. Faucet: Mustee 63.000A chrome mop style wall hung faucet
HB1 |  | HOSE BIBB, Woodford 24, anti-siphon - vacuum breaker, wheel handle and loose tee key. Verify locations in parking garage area and trash room. Size: 3/4"
HB2 |  | HOSE BIBB, Woodford 65, non-freeze, anti-siphon -vacuum breaker, automatic draining, loose tee key handle. Verify use at exterior wall locations. Size: 3/4"
FD1 |  | FLOOR DRAIN, Watts FD33, cast iron floor drain with 8" ductile iron strainer.
DD1 |  | DECK / OVERFLOW DRAIN, Watts RD25, Combination Drain and Overflow, cast iron body with membrane flashing clamp/gravel guard, cast iron dome strainer, and roof sump receiver.
PD1 |  | PLANTER DRAIN, Watts FD15, cast iron drain with membrane flashing clamp. Connect perforated PVC riser cut to match grade inside planter and wrap with filter fabric.
TD1 |  | TRENCH DRAIN, NDS, DS-090N polyethylene drain channel with DS-231 cast iron grate at garage ramps.
FCO |  | CLEAN OUT, Floor type, Olympic Foundry M1007, round scoriated cover and frame.
FIXTURE NOTES
| 1. | Provide manufacturer's standard trim, seats, supply kits and valves as indicated on drawings and as required for complete installation.
| 2. | Provide premolded, under-sink protective pipe covers on exposed lavatories to meet ADA. Proflo PF200 or equal.
| 3. | Provide LSP V-104-A chrome angle stops, LSP, SWC-112 stainless steel braided toilet or sink supplies, Dearborn P9704 white plastic p-traps.

## 2. PLUMBING EQUIPMENT
TAG | PLUMBING EQUIPMENT SCHEDULE
OW1 | OIL SAND SEPARATOR, 36"x36" concrete basin with light truck traffic rated frame and grate. Quality Concrete Products, Inc; Mukilteo, WA. Or approved equal.
SP1 | SUMP PUMP AND BASIN, Duplex. (serves oil water separator) Submersible sump pump (passes 1/2" spherical solids), including automatic level controls, high water alarm, & basin to fit application. Pump capacity: 59 GPM @ 25' TDH. Zoeller N140 series, 1 hp sump pump and Zoeller 10-0092 control panel. Catch Basin: 36" x 36" concrete basin (Verify depth) with HD-20 wheel rated cover. Quality Concrete Products or approved equal. Electrical Data: 115/1/60, 12 FLA, 20 amp circuit. Each pump
BFP1 | BACKFLOW PREVENTER, Double check valve type with shut-off valves. Watts Model 757OSY or approved equal. Install strainer on inlet side.
BFP2 | BACKFLOW PREVENTER, Double check valve type with shut-off valves. Watts Model 007QT or approved equal. Install stainer on inlet side.
PRV1 | PRESSURE REGULATOR, automatic control valve. Watts Model F100 or approved equal.
PRV2 | PRESSURE REGULATOR, pressure reducing valve. Watts Model 223 or approved equal.

## 3. PLUMBING GENERAL NOTES
PLUMBING GENERAL NOTES
1. | CODES & PERMITS: All work per local & UPC codes. Obtain and pay for all required permits and fees.
2. | SIZES: All pipe sizes shown are minimum.
3. | CLEAN OUTS: Provide per 2009 Uniform Plumbing Code and local code.
4. | PIPE INSULATION: Armaflex, Nomaco, or approved equal. Install only where required by code.
5. | WASTE & VENT PIPING: No-hub cast iron pipe throughout building.
STORM DRAIN PIPING: Storm drain piping to be No-hub cast iron in unit framing and retail areas. Storm drain piping to be No-hub in parking garage, storage and mechanical rooms and all underground areas.
6. | WASTE SLOPE: 1/4" per foot run, except as noted.
7.
8.
9. | DOMESTIC WATER: CPVC pipe and fittings for 2.5" and larger pipe. Uponor PEX pipe and fittings for 2" and smaller water mains. Within the living units, install Uponor PEX pipe and fittings. Install on warm side of building insulation.
10. | REVIEW: All fixture and equipment locations with architectural and structural plans prior to construction and coordinate as required.
11. | UNDERGROUND PIPING: Coordinate all locations with footings and maintain 45 degree angle depth distance from footings.
12. | STUB-OUT & INVERT ELEVATIONS: Verify & coordinate with civil plans and with final field conditions.
13. | WATER HAMMER ARRESTORS: Provide as required by UPC. Size per manufacturer’s recommendations. Sioux Chief, PPP Inc, LSP or approved equal.
14. | TRAP PRIMERS/SEALS: Provide where required by local code. PPP Inc., ProFlo, SureSeal or approved equal.
15. | SEWER CONNECTION: Connect waste to sanitary sewer. Field locate and verify existing size and capacity.
16. | DIELECTRIC CONNECTIONS: Provide between dissimilar metals.
17. | SEISMIC BRACING: Anchor or strap water heaters over 4'-0" in height (from base to top of tank) to resist horizontal displacement.
18. | PIPE HANGERS: Swivel loop style, Erico Model 100/115 or equal brand, with allthread steel rod sized per industry standards.
19. | GAS PIPE: Schedule 40, threaded black steel. Paint pipe exposed to weather.
20. | FREEZE PROTECTION: Make adequate provision to protect pipes from freezing in exterior walls, attics and crawl spaces. 2009 UPC.
21. | FIRE STOPPING: Install ProSet or equal firestop sleeves at pipe penetations of post-tension decks. Fire stopping in wood frame to be supplied by others.
22. | AREA SEPARATION WALLS: No vent penetrations within 5 feet of either side of area separation walls.
23. | ROUTING of lines is partially schematic and may be changed by the contractor for more efficient installation. Verify with the architect where proposed changes will be made before relocating & coordinate with other trades. Indicate all changes on “As-Built” plans and return “As-Built” drawings to the architect.

## 4. PLUMBING CONNECTION SCHEDULE
PLUMBING CONNECTION SCHEDULE
| FIXURE | MIN. PLUMBING CONNECTIONS (INCHES)
|  | CW | HW | W | V
| WATER CLOSET - FLUSH TANK | 0.5 | -- | 3 | 2
| WATER CLOSET - FLUSH VALVE | 1 | -- | 3 | 2
| URINAL | 0.75 | -- | 2 | 1-1/2
| SHOWER/TUB | 0.5 | 0.5 | 2 | 1-1/2
| LAVATORY, COUNTERTOP | 0.5 | 0.5 | 1-1/2 | 1-1/2
| SINK | 0.5 | 0.5 | 2 | 1-1/2
| DRINKING FOUNTAIN | 0.5 | -- | 1-1/4 | 1-1/4
| LAUNDRY TUB | 0.5 | 0.5 | 2 | 1-1/2
| JANITOR SINK | 0.75 | 0.75 | 3 | 1-1/2
| WASHER CONNECTION - RESID. | 0.5 | 0.5 | 2 | 1-1/2
| WATER COOLER | 0.375 | -- | 1-1/2 | 1-1/4
| HOSE BIBB | 0.5 | -- | -- | --
| FLOOR DRAIN | -- | -- | 2 | 1-1/2
| FLOOR SINK | -- | -- | 2 | 1-1/2

## 5. NATURAL GAS LOADS
NATURAL GAS LOADS
QTY | ITEM | MBH | MBH