## 1. PLUMBING FIXTURE
TAG |  | PLUMBING FIXTURE SCHEDULE
P1 |  | WATER CLOSET, FLUSH TANK, Kohler K3997, gravity flush tank, round front, 1.28 gpf, vitreous china, white. Seat: Kohler K4775, round front, with cover. LSP V104-A brass angle stop and LSP SWC-112-PP braided stainless steel supply.
P2 |  | WATER CLOSET, FLUSH TANK, Kohler K3609, gravity flush tank, 17" high, elongated, 1.28 gpf, vitreous china, white. Install to meet ADA as required. Seat: Kohler K4774, elongated, with cover. LSP V104-A brass angle stop and LSP SWC-112-PP braided stainless steel supply.
P3 |  | LAVATORY, COUNTERTOP, Kohler K2699-4, 20x17, 4" centers, self rimming, vitreous china, white. Install to meet ADA as required. Faucet: Kohler K15182-F, single lever, 1.5 gpm, with pop-up waste assembly. Dearborn P9704 p-trap and LSP V104-A brass angle stops.
P4 |  | BATHTUB/SHOWER COMBO, Aquatic 2603CT, 60"Wx32"Dx72"H, 1-piece fiberglass tub/shower stall. Tub/Shower Trim Kit: Kohler KT15601-4SH, chrome, single handle, 1.5 gpm shower head, diverter slip tub spout, with Kohler K304UX pressure balance valve. Tub drain kit: LSP R-6011RK/R0910 chrome waste and overflow assembly.
P5 |  | BATHTUB/SHOWER COMBO, Aquatic 2603CTH, 60"Wx32"Dx72"H, 1-piece fiberglass tub/shower stall with grab bars and folding seat. Tub/Shower Trim Kit: Kohler KT15601-4S, chrome, single handle, diverter slip tub spout, with Kohler K304UX pressure balance valve. Tub drain kit: LSP R-6011RK/R0910 chrome waste and overflow assembly. Handheld Shower: Moen 57210EP, chrome, 1.5 gpm head with slide bar. Provide ADA requirements.
P6 |  | SINK, SINGLE BOWL, Kohler K3348-4, 25"Wx22"Dx7.0"H, self-rim, 19 gauge stainless steel. Faucet: Kohler K596-CP, chrome, single lever handle with pull-down spray head, 1.8 gpm. Dearborn P9704 p-trap and LSP V104-A brass angle stop. ISE Badger 5 garage disposal with pigtail.
P7 |  | DISHWASHER, LSP V104-A chrome angle stop with LSP KDW-660-PP flexible supply. Install Zurn CD4P plastic countertop mount airgap.
P8 |  | ICEMAKER CONNECTION-RESIDENTIAL TYPE, Sioux Chief 696 series recessed box kit with 1/2" cold shutoff valve with 1/4" connection and code approved water hammer arrestor. Install with rated box at party wall locations.
P9 |  | WASHER CONNECTION - RESIDENTIAL TYPE, Sioux Chief 696 series recessed washer box kit with 2" drain, 1/2" hot & cold shutoff valves with hose connections and code approved water hammer arrestors. Install with rated box at party wall locations.
P10 |  | ELECTRIC WATER HEATER- RESIDENTIAL TANK TYPE, AO Smith ECT-52, 50-gal. water heater with 4.5 kw non-simultaneous elements, 208 volt, 1 phase. Include Oatey aluminium drip pan under each heater. Include insulation pad to meet code. Include ProFlo PFXT5 expansion tank. Include earthquake strap kit.
P11 |  | ELECTRIC WATER HEATER-TANKLESS TYPE, Eemax EX8208 on-demand tankless water heater to serve amenity sinks or lavatories. 208 volt, 8.3 kw, 40 amps.
P12 |  | LAVATORY, WALL HUNG, (Lobby leasing restroom) Kohler K2005, 21x18, 4" centers, wall mount, vitreous china, white. Install to meet ADA as required. Faucet: Kohler K15597-F, single lever, 0.5 gpm, with grid drain waste assembly.
P13 |  | ELECTRIC WATER HEATER, (Amenity room sink) AO Smith EJC-10, 10-gallon water heater with 1600 watt element, 120 volt, 1-phase electric water heater located inside sink cabinet to serve amenity room sink and dishwasher.
HB1 |  | HOSE BIBB, Woodford 24, anti-siphon - vacuum breaker, wheel handle and loose tee key. Verify use in parking garage area trash room. Size: 3/4"
HB2 |  | HOSE BIBB, Woodford 65, non-freeze, anti-siphon -vacuum breaker, automatic draining, loose tee key handle. Verify use at exterior wall locations. Size: 3/4"
GD-1 |  | GARAGE FLOOR DRAIN, Quality Concrete CB20, 12"x12" concrete garage floor drain/basin. Drain to oil/sand separator.
FD1 |  | FLOOR DRAIN, Watts FD33, cast iron body, with ductile iron strainer assembly.
HD1 |  | HUB DRAIN, PVC, DWV plastic drain standpipe in mechanical room.
DD1 |  | DECK DRAIN, Watts R28, cast iron body, with cast iron dome strainer under deck paver system.
DD2 |  | DECK DRAIN, Watts RD25, cast iron body, drain with overflow under deck paver system. Includes cast iron dome strainers.
TD1 |  | TRENCH DRAIN, NDS DS-090N, polyethylene trench with DS231 cast iron grate.
FCO |  | CLEAN OUT, Floor type, Olympic Foundry M1007, round scoriated cover and frame.
FIXTURE NOTES
| 1. | Provide manufacturer's standard trim, seats, supply kits and valves as indicated on drawings and as required for complete installation.
| 2. | Provide premolded, under-sink protective pipe covers on exposed lavatories to meet ADA. Proflo PF200 or equal.
| 3. | Provide LSP V-104-A chrome angle stops, LSP, SWC-112 stainless steel braided toilet or sink supplies, Dearborn P9704 white plastic p-traps.

## 2. PLUMBING EQUIPMENT
TAG | PLUMBING EQUIPMENT SCHEDULE
OW1 | OIL SAND SEPARATOR, 36"x36" concrete basin with light truck traffic rated frame and grate. Quality Concrete Products, Inc; Mukiteo, WA.
BV | BACKWATER VALVE, Canplas or equal PVC backwater valve to match pipe size. Install Quality Concrete, concrete access box with cast iron cover.
BFP1 | BACKFLOW PREVENTER, Reduced pressure type with shut-off valves. Watts Model 957OSY or approved equal.
BFP2 | BACKFLOW PREVENTER, Reduced pressure type with shut-off valves. Watts Model 009QT or approved equal.
BFP3 | BACKFLOW PREVENTER, Reduced pressure type with shut-off valves. Watts Model 009QT or approved equal.
PRV1 | PRESSURE REGULATOR, automatic control valve. Watts Model F100 or approved equal.
PRV2 | PRESSURE REGULATOR, pressure reducing valve. Watts Model 223 or approved equal.

## 3. PLUMBING GENERAL NOTES
PLUMBING GENERAL NOTES
1. | CODES & PERMITS: All work per local & state codes. Obtain and pay for all required permits and fees.
2. | SIZES: All pipe sizes shown are minimum.
3. | CLEAN OUTS: Provide per 2009 Uniform Plumbing Code and local code.
4. | INSULATION: Armaflex, Nomaco foam cell, Johns Manville Microlok or approved equal. Install only where required by code.
5. | WASTE & VENT PIPING: Waste stacks to be no-hub cast iron pipe and fittings within live/work units and leasing office/lobby ceilings. Waste piping in all other areas to be PVC, DWV plastic pipe and fittings. Vent piping throughout building to be PVC DWV plastic pipe and fittings.
6. | STORM DRAIN PIPING: Storm drain piping to be PVC, DWV plastic.
7. | FOOTING DRAIN PIPING: 4" perforated, solvent weld SDR-35 PVC plastic pipe, per ASTM D1784, with 2" PVC pickups to shoring wall drain mat.
8. | METHANE VENT PIPING: 4" perforated, solvent weld SDR-35 PVC plastic pipe, with 4" PVC solid wall piping above slab on grade through rooftop outlet.
9. | DOMESTIC WATER: CPVC pipe and fittings for 2.5" and larger pipe. Uponor PEX pipe and fittings for 2" and smaller water mains. Within the living units, install Uponor PEX pipe and fittings. Install on warm side of building insulation.
10. | REVIEW: All fixture and equipment locations with architectural and structural plans prior to construction and coordinate as required.
11. | UNDERGROUND PIPING: Coordinate all locations with footings and maintain 45 degree angle depth distance from footings.
12. | STUB-OUT & INVERT ELEVATIONS: Verify & coordinate with civil plans and with final field conditions.
13. | WATER HAMMER ARRESTORS: Provide as required by UPC. Size per manufacturer’s recommendations. Sioux Chief, PPP Inc, LSP or approved equal.
14. | TRAP PRIMERS/SEALS: Provide where required by local code. PPP Inc., ProFlo, SureSeal or approved equal.
15. | SEWER CONNECTION: Connect waste to sanitary sewer. Field locate and verify existing size and capacity.
16. | DIELECTRIC CONNECTIONS: Provide between dissimilar metals.
17. | SEISMIC BRACING: Anchor or strap water heaters over 4'-0" in height (from base to top of tank) to resist horizontal displacement.
18. | PIPE HANGERS: Swivel loop style, Erico Model 100/115 or equal brand, with allthread steel rod sized per industry standards.
19.
20. | FREEZE PROTECTION: Make adequate provision to protect pipes from freezing in exterior walls, attics and crawl spaces. 2009 UPC.
21. | FIRE STOPPING: Verify proper fire stopping thru fire and smoke rated assemblies as required by local and state code.
22. | AREA SEPARATION WALLS: No vent penetrations within 5 feet of either side of area separation walls.
23. | ROUTING of lines is partially schematic and may be changed by the contractor for more efficient installation. Verify with the architect where proposed changes will be made before relocating & coordinate with other trades. Indicate all changes on “As-Built” plans and return “As-Built” drawings to the architect.

## 4. PLUMBING CONNECTION SCHEDULE
PLUMBING CONNECTION SCHEDULE
| FIXURE | MIN. PLUMBING CONNECTIONS (INCHES)
|  | CW | HW | W | V
| WATER CLOSET - FLUSH TANK | 0.5 | -- | 3 | 2
| WATER CLOSET - FLUSH VALVE | 1 | -- | 3 | 2
| URINAL | 0.75 | -- | 2 | 1-1/2
| SHOWER/TUB | 0.5 | 0.5 | 2 | 1-1/2
| LAVATORY, COUNTERTOP | 0.5 | 0.5 | 1-1/2 | 1-1/2
| SINK | 0.5 | 0.5 | 2 | 1-1/2
| DRINKING FOUNTAIN | 0.5 | -- | 1-1/4 | 1-1/4
| LAUNDRY TUB | 0.5 | 0.5 | 2 | 1-1/2
| JANITOR SINK | 0.75 | 0.75 | 3 | 1-1/2
| WASHER CONNECTION - RESID. | 0.5 | 0.5 | 2 | 1-1/2
| WATER COOLER | 0.375 | -- | 1-1/2 | 1-1/4
| HOSE BIBB | 0.5 | -- | -- | --

## 5. NATURAL GAS LOADS
NATURAL GAS LOADS
QTY | ITEM | MBH | MBH